## Sheet1
16bit input registers (modbus function code 4)
address |  |  | type | units | description | channel
dec | hex
0 | 0x | 000 | float | Amperes | instant current | 1
1 | 0x | 001
2 | 0x | 002 | float | Amperes | instant current | 2
3 | 0x | 003
4 | 0x | 004 | float | Amperes | instant current | 3
5 | 0x | 005
6 | 0x | 006 | float | Amperes | instant current | 4
7 | 0x | 007
8 | 0x | 008 | float | Amperes | instant current | 5
9 | 0x | 009
10 | 0x | 00A | float | Amperes | instant current | 6
11 | 0x | 00B
12 | 0x | 00C | float | Amperes | instant current | 7
13 | 0x | 00D
14 | 0x | 00E | float | Amperes | instant current | 8
15 | 0x | 00F
16 | 0x | 010 | float | Amperes | instant current | 9
17 | 0x | 011
18 | 0x | 012 | float | Amperes | instant current | 10
19 | 0x | 013
20 | 0x | 014 | float | Amperes | instant current | 11
21 | 0x | 015
22 | 0x | 016 | float | Amperes | instant current | 12
23 | 0x | 017
24 | 0x | 018 | float | Amperes | instant current | 13
25 | 0x | 019
26 | 0x | 01A | float | Amperes | instant current | 14
27 | 0x | 01B
28 | 0x | 01C | float | Amperes | instant current | 15
29 | 0x | 01D
30 | 0x | 01E | float | Amperes | instant current | 16
31 | 0x | 01F
32 | 0x | 020 | float | Amperes | instant current | 17
33 | 0x | 021
34 | 0x | 022 | float | Amperes | instant current | 18
35 | 0x | 023
36 | 0x | 024 | float | Amperes | instant current | 19
37 | 0x | 025
38 | 0x | 026 | float | Amperes | instant current | 20
39 | 0x | 027
40 | 0x | 028 | float | Amperes | instant current | 21
41 | 0x | 029
42 | 0x | 02A | float | Amperes | instant current | 22
43 | 0x | 02B
44 | 0x | 02C | float | Amperes | instant current | 23
45 | 0x | 02D
46 | 0x | 02E | float | Amperes | instant current | 24
47 | 0x | 02F
48 | 0x | 030 | float |  | not used – returns zero
49 | 0x | 031
50 | 0x | 032 | float |  | instant current
51 | 0x | 033
52 | 0x | 034 | float |  | instant current
53 | 0x | 035
54 | 0x | 036 | float |  | instant current
55 | 0x | 037
56 | 0x | 038 | float |  | instant current
57 | 0x | 039
58 | 0x | 03A | float |  | instant current
59 | 0x | 03B
60 | 0x | 03C | float |  | instant current
61 | 0x | 03D
62 | 0x | 03E | float |  | instant current
63 | 0x | 03F
64 | 0x | 040 | float | Amperes | current averaged | 1
65 | 0x | 041
66 | 0x | 042 | float | Amperes | instant current | 2
67 | 0x | 043
68 | 0x | 044 | float | Amperes | instant current | 3
69 | 0x | 045
70 | 0x | 046 | float | Amperes | instant current | 4
71 | 0x | 047
72 | 0x | 048 | float | Amperes | instant current | 5
73 | 0x | 049
74 | 0x | 04A | float | Amperes | instant current | 6
75 | 0x | 04B
76 | 0x | 04C | float | Amperes | instant current | 7
77 | 0x | 04D
78 | 0x | 04E | float | Amperes | instant current | 8
79 | 0x | 04F
80 | 0x | 050 | float | Amperes | current averaged | 9
81 | 0x | 051
82 | 0x | 052 | float | Amperes | instant current | 10
83 | 0x | 053
84 | 0x | 054 | float | Amperes | instant current | 11
85 | 0x | 055
86 | 0x | 056 | float | Amperes | instant current | 12
87 | 0x | 057
88 | 0x | 058 | float | Amperes | instant current | 13
89 | 0x | 059
90 | 0x | 05A | float | Amperes | instant current | 14
91 | 0x | 05B
92 | 0x | 05C | float | Amperes | instant current | 15
93 | 0x | 05D
94 | 0x | 05E | float | Amperes | instant current | 16
95 | 0x | 05F
96 | 0x | 060 | float | Amperes | current averaged | 17
97 | 0x | 061
98 | 0x | 062 | float | Amperes | instant current | 18
99 | 0x | 063
100 | 0x | 064 | float | Amperes | instant current | 19
101 | 0x | 065
102 | 0x | 066 | float | Amperes | instant current | 20
103 | 0x | 067
104 | 0x | 068 | float | Amperes | instant current | 21
105 | 0x | 069
106 | 0x | 06A | float | Amperes | instant current | 22
107 | 0x | 06B
108 | 0x | 06C | float | Amperes | instant current | 23
109 | 0x | 06D
110 | 0x | 06E | float | Amperes | instant current | 24
111 | 0x | 06F
112 | 0x | 070 | float |  | not used – returns zero
113 | 0x | 071
114 | 0x | 072 | float |  | instant current
115 | 0x | 073
116 | 0x | 074 | float |  | instant current
117 | 0x | 075
118 | 0x | 076 | float |  | instant current
119 | 0x | 077
120 | 0x | 078 | float |  | instant current
121 | 0x | 079
122 | 0x | 07A | float |  | instant current
123 | 0x | 07B
124 | 0x | 07C | float |  | instant current
125 | 0x | 07D
126 | 0x | 07E | float |  | instant current
127 | 0x | 07F
128 | 0x | 080 | float | Amperes | current squared averaged | 1
129 | 0x | 081
130 | 0x | 082 | float | Amperes | instant current | 2
131 | 0x | 083
132 | 0x | 084 | float | Amperes | instant current | 3
133 | 0x | 085
134 | 0x | 086 | float | Amperes | instant current | 4
135 | 0x | 087
136 | 0x | 088 | float | Amperes | instant current | 5
137 | 0x | 089
138 | 0x | 08A | float | Amperes | instant current | 6
139 | 0x | 08B
140 | 0x | 08C | float | Amperes | instant current | 7
141 | 0x | 08D
142 | 0x | 08E | float | Amperes | instant current | 8
143 | 0x | 08F
144 | 0x | 090 | float | Amperes | current squared averaged | 9
145 | 0x | 091
146 | 0x | 092 | float | Amperes | instant current | 10
147 | 0x | 093
148 | 0x | 094 | float | Amperes | instant current | 11
149 | 0x | 095
150 | 0x | 096 | float | Amperes | instant current | 12
151 | 0x | 097
152 | 0x | 098 | float | Amperes | instant current | 13
153 | 0x | 099
154 | 0x | 09A | float | Amperes | instant current | 14
155 | 0x | 09B
156 | 0x | 09C | float | Amperes | instant current | 15
157 | 0x | 09D
158 | 0x | 09E | float | Amperes | instant current | 16
159 | 0x | 09F
160 | 0x | 0A0 | float | Amperes | current squared averaged | 17
161 | 0x | 0A1
162 | 0x | 0A2 | float | Amperes | instant current | 18
163 | 0x | 0A3
164 | 0x | 0A4 | float | Amperes | instant current | 19
165 | 0x | 0A5
166 | 0x | 0A6 | float | Amperes | instant current | 20
167 | 0x | 0A7
168 | 0x | 0A8 | float | Amperes | instant current | 21
169 | 0x | 0A9
170 | 0x | 0AA | float | Amperes | instant current | 22
171 | 0x | 0AB
172 | 0x | 0AC | float | Amperes | instant current | 23
173 | 0x | 0AD
174 | 0x | 0AE | float | Amperes | instant current | 24
175 | 0x | 0AF
176 | 0x | 0B0 | float |  | not used – returns zero
177 | 0x | 0B1
178 | 0x | 0B2 | float |  | instant current
179 | 0x | 0B3
180 | 0x | 0B4 | float |  | instant current
181 | 0x | 0B5
182 | 0x | 0B6 | float |  | instant current
183 | 0x | 0B7
184 | 0x | 0B8 | float |  | instant current
185 | 0x | 0B9
186 | 0x | 0BA | float |  | instant current
187 | 0x | 0BB
188 | 0x | 0BC | float |  | instant current
189 | 0x | 0BD
190 | 0x | 0BE | float |  | instant current
191 | 0x | 0BF
192 | 0x | 0C0 | float | Amperes | current holded values | 1
193 | 0x | 0C1
194 | 0x | 0C2 | float | Amperes | instant current | 2
195 | 0x | 0C3
196 | 0x | 0C4 | float | Amperes | instant current | 3
197 | 0x | 0C5
198 | 0x | 0C6 | float | Amperes | instant current | 4
199 | 0x | 0C7
200 | 0x | 0C8 | float | Amperes | instant current | 5
201 | 0x | 0C9
202 | 0x | 0CA | float | Amperes | instant current | 6
203 | 0x | 0CB
204 | 0x | 0CC | float | Amperes | instant current | 7
205 | 0x | 0CD
206 | 0x | 0CE | float | Amperes | instant current | 8
207 | 0x | 0CF
208 | 0x | 0D0 | float | Amperes | current holded values | 9
209 | 0x | 0D1
210 | 0x | 0D2 | float | Amperes | instant current | 10
211 | 0x | 0D3
212 | 0x | 0D4 | float | Amperes | instant current | 11
213 | 0x | 0D5
214 | 0x | 0D6 | float | Amperes | instant current | 12
215 | 0x | 0D7
216 | 0x | 0D8 | float | Amperes | instant current | 13
217 | 0x | 0D9
218 | 0x | 0DA | float | Amperes | instant current | 14
219 | 0x | 0DB
220 | 0x | 0DC | float | Amperes | instant current | 15
221 | 0x | 0DD
222 | 0x | 0DE | float | Amperes | instant current | 16
223 | 0x | 0DF
224 | 0x | 0E0 | float | Amperes | current holded values | 17
225 | 0x | 0E1
226 | 0x | 0E2 | float | Amperes | instant current | 18
227 | 0x | 0E3
228 | 0x | 0E4 | float | Amperes | instant current | 19
229 | 0x | 0E5
230 | 0x | 0E6 | float | Amperes | instant current | 20
231 | 0x | 0E7
232 | 0x | 0E8 | float | Amperes | instant current | 21
233 | 0x | 0E9
234 | 0x | 0EA | float | Amperes | instant current | 22
235 | 0x | 0EB
236 | 0x | 0EC | float | Amperes | instant current | 23
237 | 0x | 0ED
238 | 0x | 0EE | float | Amperes | instant current | 24
239 | 0x | 0EF
240 | 0x | 0F0 | float |  | not used – returns zero
241 | 0x | 0F1
242 | 0x | 0F2 | float |  | instant current
243 | 0x | 0F3
244 | 0x | 0F4 | float |  | instant current
245 | 0x | 0F5
246 | 0x | 0F6 | float |  | instant current
247 | 0x | 0F7
248 | 0x | 0F8 | float |  | instant current
249 | 0x | 0F9
250 | 0x | 0FA | float |  | instant current
251 | 0x | 0FB
252 | 0x | 0FC | float |  | instant current
253 | 0x | 0FD
254 | 0x | 0FE | float |  | instant current
255 | 0x | 0FF
256 | 0x | 100 | float | Celcious | temperature
257 | 0x | 101
258 | 0x | 102 | float | Volt | system voltage
259 | 0x | 103
260 | 0x | 104 | float | Volt | system voltage averaged value
261 | 0x | 105
262 | 0x | 106 | float | Volt | system voltage holded value
263 | 0x | 107
264 | 0x | 108 | float | kWatt | instant total power
265 | 0x | 109
266 | 0x | 10A | float | kWatt | averaged total power
267 | 0x | 10B
268 | 0x | 10C | float | kWatt | holded total power
269 | 0x | 10D
270 | 0x | 10E | float | kWH | total energy Of last period
271 | 0x | 10F
272 | 0x | 110 | unsigned long int | csec | time of last period
273 | 0x | 111
274 | 0x | 112 | unsigned long int | csec | time since last mark
275 | 0x | 113
320 | 0x | 140 | float | kWatt | instant power | 1
321 | 0x | 141
322 | 0x | 142 | float | kWatt | instant current | 2
323 | 0x | 143
324 | 0x | 144 | float | kWatt | instant current | 3
325 | 0x | 145
326 | 0x | 146 | float | kWatt | instant current | 4
327 | 0x | 147
328 | 0x | 148 | float | kWatt | instant current | 5
329 | 0x | 149
330 | 0x | 14A | float | kWatt | instant current | 6
331 | 0x | 14B
332 | 0x | 14C | float | kWatt | instant current | 7
333 | 0x | 14D
334 | 0x | 14E | float | kWatt | instant current | 8
335 | 0x | 14F
336 | 0x | 150 | float | kWatt | current holded values | 9
337 | 0x | 151
338 | 0x | 152 | float | kWatt | instant current | 10
339 | 0x | 153
340 | 0x | 154 | float | kWatt | instant current | 11
341 | 0x | 155
342 | 0x | 156 | float | kWatt | instant current | 12
343 | 0x | 157
344 | 0x | 158 | float | kWatt | instant current | 13
345 | 0x | 159
346 | 0x | 15A | float | kWatt | instant current | 14
347 | 0x | 15B
348 | 0x | 15C | float | kWatt | instant current | 15
349 | 0x | 15D
350 | 0x | 15E | float | kWatt | instant current | 16
351 | 0x | 15F
352 | 0x | 160 | float | kWatt | current holded values | 17
353 | 0x | 161
354 | 0x | 162 | float | kWatt | instant current | 18
355 | 0x | 163
356 | 0x | 164 | float | kWatt | instant current | 19
357 | 0x | 165
358 | 0x | 166 | float | kWatt | instant current | 20
359 | 0x | 167
360 | 0x | 168 | float | kWatt | instant current | 21
361 | 0x | 169
362 | 0x | 16A | float | kWatt | instant current | 22
363 | 0x | 16B
364 | 0x | 16C | float | kWatt | instant current | 23
365 | 0x | 16D
366 | 0x | 16E | float | kWatt | instant current | 24
367 | 0x | 16F
368 | 0x | 170 | float |  | not used – returns zero
369 | 0x | 171
370 | 0x | 172 | float |  | instant current
371 | 0x | 173
372 | 0x | 174 | float |  | instant current
373 | 0x | 175
374 | 0x | 176 | float |  | instant current
375 | 0x | 177
376 | 0x | 178 | float |  | instant current
377 | 0x | 179
378 | 0x | 17A | float |  | instant current
379 | 0x | 17B
380 | 0x | 17C | float |  | instant current
381 | 0x | 17D
382 | 0x | 17E | float |  | instant current
383 | 0x | 17F
384 | 0x | 180 | float | kWatt | power averaged values | 1
385 | 0x | 181
386 | 0x | 182 | float | kWatt | instant current | 2
387 | 0x | 183
388 | 0x | 184 | float | kWatt | instant current | 3
389 | 0x | 185
390 | 0x | 186 | float | kWatt | instant current | 4
391 | 0x | 187
392 | 0x | 188 | float | kWatt | instant current | 5
393 | 0x | 189
394 | 0x | 18A | float | kWatt | instant current | 6
395 | 0x | 18B
396 | 0x | 18C | float | kWatt | instant current | 7
397 | 0x | 18D
398 | 0x | 18E | float | kWatt | instant current | 8
399 | 0x | 18F
400 | 0x | 190 | float | kWatt | current holded values | 9
401 | 0x | 191
402 | 0x | 192 | float | kWatt | instant current | 10
403 | 0x | 193
404 | 0x | 194 | float | kWatt | instant current | 11
405 | 0x | 195
406 | 0x | 196 | float | kWatt | instant current | 12
407 | 0x | 197
408 | 0x | 198 | float | kWatt | instant current | 13
409 | 0x | 199
410 | 0x | 19A | float | kWatt | instant current | 14
411 | 0x | 19B
412 | 0x | 19C | float | kWatt | instant current | 15
413 | 0x | 19D
414 | 0x | 19E | float | kWatt | instant current | 16
415 | 0x | 19F
416 | 0x | 1A0 | float | kWatt | current holded values | 17
417 | 0x | 1A1
418 | 0x | 1A2 | float | kWatt | instant current | 18
419 | 0x | 1A3
420 | 0x | 1A4 | float | kWatt | instant current | 19
421 | 0x | 1A5
422 | 0x | 1A6 | float | kWatt | instant current | 20
423 | 0x | 1A7
424 | 0x | 1A8 | float | kWatt | instant current | 21
425 | 0x | 1A9
426 | 0x | 1AA | float | kWatt | instant current | 22
427 | 0x | 1AB
428 | 0x | 1AC | float | kWatt | instant current | 23
429 | 0x | 1AD
430 | 0x | 1AE | float | kWatt | instant current | 24
431 | 0x | 1AF
432 | 0x | 1B0 | float |  | not used – returns zero
433 | 0x | 1B1
434 | 0x | 1B2 | float |  | instant current
435 | 0x | 1B3
436 | 0x | 1B4 | float |  | instant current
437 | 0x | 1B5
438 | 0x | 1B6 | float |  | instant current
439 | 0x | 1B7
440 | 0x | 1B8 | float |  | instant current
441 | 0x | 1B9
442 | 0x | 1BA | float |  | instant current
443 | 0x | 1BB
444 | 0x | 1BC | float |  | instant current
445 | 0x | 1BD
446 | 0x | 1BE | float |  | instant current
447 | 0x | 1BF
448 | 0x | 1C0 | float | kWatt | power holded values | 1
449 | 0x | 1C1
450 | 0x | 1C2 | float | kWatt | instant current | 2
451 | 0x | 1C3
452 | 0x | 1C4 | float | kWatt | instant current | 3
453 | 0x | 1C5
454 | 0x | 1C6 | float | kWatt | instant current | 4
455 | 0x | 1C7
456 | 0x | 1C8 | float | kWatt | instant current | 5
457 | 0x | 1C9
458 | 0x | 1CA | float | kWatt | instant current | 6
459 | 0x | 1CB
460 | 0x | 1CC | float | kWatt | instant current | 7
461 | 0x | 1CD
462 | 0x | 1CE | float | kWatt | instant current | 8
463 | 0x | 1CF
464 | 0x | 1D0 | float | kWatt | current holded values | 9
465 | 0x | 1D1
466 | 0x | 1D2 | float | kWatt | instant current | 10
467 | 0x | 1D3
468 | 0x | 1D4 | float | kWatt | instant current | 11
469 | 0x | 1D5
470 | 0x | 1D6 | float | kWatt | instant current | 12
471 | 0x | 1D7
472 | 0x | 1D8 | float | kWatt | instant current | 13
473 | 0x | 1D9
474 | 0x | 1DA | float | kWatt | instant current | 14
475 | 0x | 1DB
476 | 0x | 1DC | float | kWatt | instant current | 15
477 | 0x | 1DD
478 | 0x | 1DE | float | kWatt | instant current | 16
479 | 0x | 1DF
480 | 0x | 1E0 | float | kWatt | current holded values | 17
481 | 0x | 1E1
482 | 0x | 1E2 | float | kWatt | instant current | 18
483 | 0x | 1E3
484 | 0x | 1E4 | float | kWatt | instant current | 19
485 | 0x | 1E5
486 | 0x | 1E6 | float | kWatt | instant current | 20
487 | 0x | 1E7
488 | 0x | 1E8 | float | kWatt | instant current | 21
489 | 0x | 1E9
490 | 0x | 1EA | float | kWatt | instant current | 22
491 | 0x | 1EB
492 | 0x | 1EC | float | kWatt | instant current | 23
493 | 0x | 1ED
494 | 0x | 1EE | float | kWatt | instant current | 24
495 | 0x | 1EF
496 | 0x | 1F0 | float |  | not used – returns zero
497 | 0x | 1F1
498 | 0x | 1F2 | float |  | instant current
499 | 0x | 1F3
500 | 0x | 1F4 | float |  | instant current
501 | 0x | 1F5
502 | 0x | 1F6 | float |  | instant current
503 | 0x | 1F7
504 | 0x | 1F8 | float |  | instant current
505 | 0x | 1F9
506 | 0x | 1FA | float |  | instant current
507 | 0x | 1FB
508 | 0x | 1FC | float |  | instant current
509 | 0x | 1FD
510 | 0x | 1FE | float |  | instant current
511 | 0x | 1FF
512 | 0x | 200 | float | kWH | energy of the last period | 1
513 | 0x | 201
514 | 0x | 202 | float | kWH | instant current | 2
515 | 0x | 203
516 | 0x | 204 | float | kWH | instant current | 3
517 | 0x | 205
518 | 0x | 206 | float | kWH | instant current | 4
519 | 0x | 207
520 | 0x | 208 | float | kWH | instant current | 5
521 | 0x | 209
522 | 0x | 20A | float | kWH | instant current | 6
523 | 0x | 20B
524 | 0x | 20C | float | kWH | instant current | 7
525 | 0x | 20D
526 | 0x | 20E | float | kWH | instant current | 8
527 | 0x | 20F
528 | 0x | 210 | float | kWH | current holded values | 9
529 | 0x | 211
530 | 0x | 212 | float | kWH | instant current | 10
531 | 0x | 213
532 | 0x | 214 | float | kWH | instant current | 11
533 | 0x | 215
534 | 0x | 216 | float | kWH | instant current | 12
535 | 0x | 217
536 | 0x | 218 | float | kWH | instant current | 13
537 | 0x | 219
538 | 0x | 21A | float | kWH | instant current | 14
539 | 0x | 21B
540 | 0x | 21C | float | kWH | instant current | 15
541 | 0x | 21D
542 | 0x | 21E | float | kWH | instant current | 16
543 | 0x | 21F
544 | 0x | 220 | float | kWH | current holded values | 17
545 | 0x | 221
546 | 0x | 222 | float | kWH | instant current | 18
547 | 0x | 223
548 | 0x | 224 | float | kWH | instant current | 19
549 | 0x | 225
550 | 0x | 226 | float | kWH | instant current | 20
551 | 0x | 227
552 | 0x | 228 | float | kWH | instant current | 21
553 | 0x | 229
554 | 0x | 22A | float | kWH | instant current | 22
555 | 0x | 22B
556 | 0x | 22C | float | kWH | instant current | 23
557 | 0x | 22D
558 | 0x | 22E | float | kWH | instant current | 24
559 | 0x | 22F
560 | 0x | 230 | float |  | not used – returns zero
561 | 0x | 231
562 | 0x | 232 | float |  | instant current
563 | 0x | 233
564 | 0x | 234 | float |  | instant current
565 | 0x | 235
566 | 0x | 236 | float |  | instant current
567 | 0x | 237
568 | 0x | 238 | float |  | instant current
569 | 0x | 239
570 | 0x | 23A | float |  | instant current
571 | 0x | 23B
572 | 0x | 23C | float |  | instant current
573 | 0x | 23D
574 | 0x | 23E | float |  | instant current
575 | 0x | 23F
Coils – digital input (modbus function code 1)
address |  |  | type | units | description
dec | hex
0 | 0x | 00 | bit | - | digital input
Holding registers – commands (modbus function code 10)
address |  |  | type | description
dec | hex
0 | 0x | 00 | Hi byte | Comands: “hold”(0x01) or “mark”(0x02) or “change address”(0x0A)
|  |  | Lo byte | if comand is “change address”, then set new target address
1 | 0x | 01 | Hi byte | if comand is “change address”, then set new target address
|  |  | Lo byte | if comand is “change address”, then set new target address